## FireDet & Conv Notification
513 | FIRE ALARM AND DETECTION SYSTEM
513.1 | General
| The fire alarm & detection system shall be an intelligent analogue expandable addressable type. The fire alarm & detection system shall be designed, installed and commissioned to achieve the following functions: i) Fire Alarm Systems with Network ii) Integrated Emergency voice communication(As Required) v) Mimic panel shall be provided for" a. Building General Fire Alarms b. Building Pressurization Fans Status (As required Item iv) c. Building Car Park Fans Status( As required item iv) d. Other Key equipment controlled by the Fire Alarm Systems iv) Integrated Multiplex Fan Control systems from the fire Alarm panel(As Required) iii) Integrated Fireman’s telephone system or equivalent(As Required) |  | Comply
| The fire alarm and detection system shall comprise of , main fire alarm panel, repeater fire alarm panel, initiating devices, manual call points, notification signaling devices, multiplex fan control interface, wiring and all related accessories based on the most recent proven technology for both hardware and software to implement complete and functional systems designed to meet the requirements as outlined in this specification. |  | Comply
| The fire alarm & detection system shall commissioned by the specialist supplier of the manufacturer as per chapter 10 of NFPA72. To ensure proper function of the complete system to the satisfaction and approval of the relevant Fire Authority and Employer. |  | Comply
| The main fire alarm panel and the detectors or interface shall be of proprietary type. All system hardware and software shall be of a type already widely used for this field of application with at least 10 years of previous installed records in Malaysia. |  | Comply
513.2 | Standards
Relevant Codes and Standards:
| Product Performance UL 864, Fire Detection and Control (UOJZ), Minimum UL268 6th Edition for Detectors Smoke Control Service (UUKL), Releasing Device Service (SYZV) FM Approved Requirement of Jabatan Bomba Dan Penyelamat Malaysia |  | Comply
| Codes and Standards NFPA72 2016/2019 Fire Detection, Voice Evac Installation, Operation and Service Codes NFPA92,92A & 92B Smoke Control systems Other codes and regulations of the local jurisdictional authorities |  | Comply
513.3 | Technical and Installation Requirements
818.3.1 System Description and Operation
|  | The fire alarm system shall incorporate the latest microcomputer technology and shall be able to achieve a satisfactory long life span. The system shall be compatible with future product upgrading and expansion. It shall also be easily integrated to other computer based systems. The system shall have the following operational features: | Comply
|  | a. The system shall automatically set the number of addresses in the system with Dip switch or equivalent. Software address not acceptable | Comply
|  | b. The address should be on the base to simplified detector cleaning operation | Comply
|  | c. The system shall be able to provide more than one level of dirt warning besides Prealarm and able to list out to clean only detector that requires cleaning for example almost dirty, dirty, excessively dirty..etc | Comply
|  | d. The system shall be able to swop Smoke with Heat detector with only trouble condition indicated on panel and revert to normal when replaced with the right detector. The heat detector when swop will be recognised by the Fire alarm panel and function accordingly. The purpose is for minor renovation work with minimum engineering cost involved and maximum life safety protection. | Comply
|  | e. It shall incorporate an alarm organization feature should it be desired to raise an alarm only if any two smoke or heat detectors are activated. | Comply
|  | f. It shall also be able to automatically store and print out upon command all detectors highest sensitivity activated versus the setpoint in their allocated environment. | Comply
|  | g. Print-outs of all types of condition shall have the date and time or occurrence. | Comply
|  | h. The main panel shall be able to show or print out the sensitively level of any detectors in the system. | Comply
|  | i. First alarms shall always to be top priority and remain in the display screen until reset. | Comply
|  | j. To allow interfacing of non-addressable devices into the main system and flow-switches thru interface modules. | Comply
|  | k. The sensitivity of all detectors shall be able to be adjusted individually at the panel and the detector itself. | Comply
|  | l. The system shall be compact stand-alone unit and capable of expanding by networking with additional Sub Alarm panels in the field as required for up to 99 panels or Workstation Servers | Comply
|  | m. The network communication shall have both option of normal hardwired base standard speed communication(9.6kBd to 57.6Kbd) or option for IP base high speed Communication and able to support Single mode fibre optic communication speed of minimum 100mbs. | Comply
|  | n. The systems shall support Graphic Workstation Server with minimum of 10 supervised or unsupervised Clients Workstation. It shall have the option of support mobile clients for both Android and Iphone and a one time mobile Client charges on the Server. There is no limitation of nos of mobile clients connections. | Comply
|  | o. The systems shall have the option of adding modules for a integrated voice evacuation and fire man phone solution. | Comply
|  | p. To provide self-diagnostic features for various system faults. | Comply
|  | q. The system shall have a minimum capacity of up to 10 loops with each loop catering for minimum 250 addressable device of any mix of Detectors or modules. | Comply
818.3.2 Quality Control
|  | a. Installer Qualifications: A factory certified and trained engineer is to supervised the installation contractor on the work of this section. | Comply
|  | b. Each and every item of the Fire Alarm System shall be listed under the appropriate category by UL and FM and shall bear the respective label. | Comply
| 818.3.3 | MAINTENANCE SERVICE
|  | a. Warranty Maintenance Service: Provide maintenance of fire alarm systems and equipment for a period of 12 months, using factory-authorized service representatives | Comply
|  | b. Basic Services: Routine maintenance visits on an “as needed” basis at times scheduled with the Owner. | Comply
|  | c. Additional Services: Perform services within the above 12-month period not classified as routine maintenance or as warranty work when authorized in writing. Compensation for additional services must be agreed upon in writing prior to performing services. | Comply
|  | d. Maintenance Service Contract: No later than 60 days prior to the expiration of the warranty maintenance services, deliver to the Owner a proposal to provide contract maintenance and repair services for an additional one-year term. | Comply
818.3.4 Fire Alarm Panel
|  | a. General: Comply with UL 864, "Control Units and Accessories for Fire Alarm Systems". UL & FM Listed The following FACU hardware shall be provided: | Comply
|  | b. Network pathways shall support RS485 hardwired, fiber optic (Single or multimode) and RJ45 as needed. | Comply
|  | c. All Fire Panel Provided need to Comply with NFPA72 Class X requirements and minimum communication speed of 12Mbps for hardwired connection. | Comply
|  | d. All Fire Alarm panels shall come with UL and FM Listing with supporting documents. | Comply
|  | e. The supplier must be able to Comply to NFPA72 2016 Chapter 7 for all documentations and NFPA72 2016 Chapter 10 for qualified manpower provision in the various stage from installations till handover. | Comply
|  | f. Able to support up to minimum of 99 Network nodes | Comply
|  | g. All Panels shall come with 32Bit CPU and with a build in minimum of 2 GB Memory card to store the related system documentation such as record drawings, record of completion, owner’s manuals, testing and maintenance records, and backup of database ….etc. or equivalent. Minimum enclosure rating shall be not less than NEMA 1 or IP30 rating. | Comply
|  | h. Minimum Panel addressable capacity shall not be less than 2,500 points that can support capacity of 2,000 addressable detectors and 500 addressable modules. Suppliers with higher point count are acceptable with minimum detector capacity as specified. | Comply
|  | i. Minimum Loop capacity shall not be less than 10 loops or greater. | Comply
|  | j. Addressable Device loops shall support non shielded or non-screen cables of recommended factory wire gauge | Comply
|  | k. The systems provided should have proven documentation by the manufacturer to prove history of backward and forward compatible records for both Panel and Devices to protect the interest of the end user. | Comply
|  | l. The system shall be provided with sufficient battery capacity to operate the entire system upon loss of normal AC power in a normal supervisory mode for a period of 24 hours with 5 minutes of alarm. | Comply
|  | m. Able to provide Integrated Voice Evacuation if function is required in future and for supplier without this feature shall provide 100 zones of input and output modules as default. | Comply
818.3.5 Fireman phone
|  | a. Firefighter's Phone: Provide a supervised, two-way communication system phones between the Command Center/main fire alarm control unit and emergency | Comply
|  | b. The firefighter's phone system shall be capable of handling single or simultaneous conversations with all phones connected into the system. | Comply
|  | c. As many as six phones shall be able to be connected into the active conversation. | Comply
|  | d. The act of plugging a handset into an emergency phone jack or removal of any phone from its normal hook position shall cause an audible and visual indication control unit. | Comply
818.3.6 System Printer
|  | a. Provide a 80 or 132 column dot-matrix type, listed and labeled as an integral part of the fire alarm system. | Comply
818.3.7 Network Annunicator Repeater
|  | a. The Repeater or Annunicator shall be a Network type and not dependant only on Main Fire Alarm Panel. | Comply
|  | b. Network pathways shall support RS485 hardwired, fiber optic (Single or multimode) and RJ45 as needed. | Comply
|  | c. All Repeater Panel Provided need to Comply with NFPA72 Class X requirements and minimum communication speed of 12Mbps for hardwired connection. | Comply
|  | d. All Repeater panels shall come with UL and FM Listing with supporting documents. | Comply
818.3.8 GRAPHIC MIMIC ANNUNCIATOR - LED TYPE
|  | a. Annunciator Unit, zoned system: Provide an LED-indicating light located on the floor plan for each zone. For each zone, mark zone boundaries on the annunciator floor plan. | Comply
|  | b. Annunciator Unit, addressable system: Provide an LED-indicating light located on the floor plan for each device indicating the type of device and floor on which a signal was actuated floor plan for each device indicating the type of device and floor on which a signal was actuated. | Comply
|  | c. Provide individual LED indicators for each alarm and supervisory device or zone and a LED to indicate system trouble. Additional LEDs indicate normal power and emergency power modes for the system. A toggle or push-button switch tests the LEDs mounted on the unit. The test switch does not require key operation. and a LED to indicate system trouble. Additional LEDs indicate normal power and emergency power modes for the system. A toggle or push-button switch tests the LEDs mounted on the unit. The test switch does not require key operation. | Comply
|  | d. Enclosure: Finish to match Fire Alarm Control Units. The locking cover/display assembly is hinged on the left. Key and lock shall be common to all secured fire alarm system enclosures. | Comply
818.3.9 NETWORK COMMAND GRAPHICAL WORKSTATION
|  | a. Able to support up to 100,000 Fire Detection points on a Workstation Server, it is not accepted to have multiple server as system operation integrity will be at risk. UL & FM Listed | Comply
|  | b. The 100,000 points shall be the full point count allocated to Fire Detection and not other systems. | Comply
|  | c. The workstation shall be linked to the Fire Alarm systems thru Class B RJ45 connections. | Comply
|  | d. PCI cards connections shall not be acceptable as they are old fashion and limited brands of support by computer supplier. | Comply
|  | e. Standard Video output for one LCD Display and able to add up to maximum of 4 LCD Display driven from one CPU Display driven from one CPU | Comply
|  | f. Each LCD Display is able to display a selected dedicated function with no interruptions from other functions e.g. Graphics only, Alarm and Fault only, History log only, IP Camera only….etc log only, IP Camera only….etc | Comply
|  | g. Integrated email Notification Service | Comply
|  | h. Field editor for graphics representations with ability to Import and Export AutoCAD graphic files | Comply
|  | i. Integrated web-page, web-camera, or web-link and able to manually display by IP address on windows or operated automatically upon Alarm points or zone | Comply
|  | j. It shall be possible to assign a different WAV file notification signal in the local language for each abnormal event. | Comply
|  | k. The Graphical Workstation shall have the capacity to annunciate 62,500 network point and/or point lists. | Comply
|  | l. Historical event logs shall maintain up to 500,000 system events. | Comply
|  | m. Built-in diagnostics shall provide graphical Diagnostic views of the network topology and status. | Comply
|  | n. Do not required PCI Slot for network card mounting. | Comply
|  | o. Capacity to create and edit up to 25,000 Graphic Screens. | Comply
|  | p. The Graphical Workstation shall come with both UL and FM Listing. | Comply
|  | q. Graphic Workstation shall not be a slave connected to Fire alarm panel to operate. | Comply
Comply
818.3.10 Remote Ethernet Client Support:
|  | a. The Graphical Workstation server shall be capable of supporting up to 20 Simultaneous Remote Client Connections over Ethernet. | Comply
|  | b. It shall be possible to vector information to Remote Supervised Clients by selecting.which points and/or event categories (Alarm, Priority 2, Supervisory, Trouble) are to be displayed at each Remote Supervised Client. | Comply
818.3.11 Mobile client Support
|  | a. The Graphical Workstation shall support both Apple iPhones and iPads, and Android phones and tablets. | Comply
|  | b. This support shall include providing fire alarm network annunciation and limited control through a compatible 3G and 4G cellular service via VPN (virtual private network) connection. | Comply
|  | c. Mobile Client Support shall connect an essentially unlimited number of Mobile Clients for simultaneous status information access. | Comply
|  | d. Limited control function shall be accessible by password controlled login and by designated mobile device. | Comply
|  | e. Display of Fire Alarm /Priority 2/Supervisory/Trouble conditions via active lists in separate tabs selection. | Comply
|  | f. Access to system silence and reset panel and Voice evac with additional level of user name and password. | Comply
818.3.12 Spare capacity
|  | Sufficient installed spare capacity shall be provided to enable the system functionality to be increased as follows: | Comply
|  | a. 20% spare detection Device loop capacity per Panel. This requirement shall ensure that all the fire alarm panels have the spare capacity to accommodate additional loops without the requirement for upgrading the complete control panel. | Comply
|  | b. 20% spare detection device capacity per loop for both Detectors and Modules Device. This requirement shall ensure that additional detection devices can be fitted to existing loops (within the restrictions of manufacturers maximum permitted loop lengths). | Comply
|  | c. 20% spare Notification circuits for any future expansion requirements by the Fire Alarm Panels. | Comply
818.3.13 ADDRESSABLE INITIATING - PullStation
|  | a. General Requirements for Manual Fire-Alarm Boxes: Comply with UL 38. Boxes shall be finished in red. UL & FM Listed | Comply
818.3.14 ADDRESSABLE INITIATING - Detectors
ADDRESSABLE ANALOG SMOKE SENSORS
|  | a. Comply with Minimum of UL 268 6th edition and Self-Restoring. UL & FM Listed | Comply
|  | b. Removal of the detector head shall cause a trouble signal at the control unit. | Comply
|  | c. Sensor address shall be located in base to simplified operations when replacing sensors. | Comply
|  | d. Upon replacement of sensor head after cleaning shall operate immediately without intervention | Comply
|  | e. Environmental compensation, programmable sensitivity settings, status testing, and monitoring of sensor dirt accumulation shall be provided by the Fire control panel. | Comply
|  | f. Options of Full Black color detector for the head and base shall be at no increase of price and not minimum order quantities | Comply
818.3.15 ADDRESSABLE INITIATING - In-DUCT SMOKE SENSOR
Addressable In-Duct Mounted Smoke Sensors - UL & FM Listed
|  | a. Photoelectric type, for applications with controlled dust and humidity providing HVAC duct smoke sensing where sampling tube designs are not appropriate. | Comply
|  | b.In-Duct housing shall include relay or relay driver as required for fan shutdown. | Comply
|  | c. Shall accommodate duct airflow from 0 to 4000 ft/min (0 to 1220 m/min), and provide environmental compensation, programmable sensitivity settings, status testing, and monitoring of sensor dirt | Comply
|  | d. Duct Housing shall have a transparent cover to monitor for the presence of smoke. | Comply
|  | e. Each duct smoke sensor shall be provided with a Remote Test Station with an alarm LED and test switch. | Comply
818.3.16 ADDRESSABLE INITIATING - Heat Detector
ADDRESSABLE HEAT SENSORS
|  | a. Comply with UL 521.- UL and FM Listed | Comply
|  | b.Thermal Sensor: Combination fixed-temperature and rate-of-rise unit with plug-in base and alarm indication lamp | Comply
|  | c. Full color Black color detector available for head and base. | Comply
|  | d. Rate-of-rise temperature detection is selectable 15° F (8.3° C) or 20° F (11.1° C) per minute. | Comply
|  | e. Fixed temperature sensing is independent of rate-of-rise sensing and programmable to operate at 135° F (57.2° C) or 155° F (68° C). | Comply
818.3.17 ADDRESSABLE CO SENSOR SOUNDER BASE - UL & FM Listed
|  | a. The CO Sensor Sounder base shall be listed to UL464, Audible Signal Appliances. | Comply
|  | b.CO sensor shall provide enhanced fire detection with the addition of two selectable modes of operation: Nuisance Alarm Reduction Mode and Faster Fire Detection. | Comply
|  | c. The CO Sensor Sounder Base shall include CO sensor element mounted in the sounder base which can be easily replaced without replacing the complete sensor base assembly. | Comply
|  | d. The CO Sensor Sounder base shall report the following CO Sensor troubles: Communication loss, Disabled, Almost Expired 12 Months, Almost Expired 6 Months, Expired (End of Life), and Sensor Missing/Failed. | Comply
|  | e. CO Base can be used with any combination of Heat only, Photo only or Photo and Heat. | Comply
818.3.18 ADDRESSABLE MULTI-POINT/MULTI-SENSOR/MULTI-CRITERIA SENSOR
|  | a. Smoke and heat sensing shall be available to be combined in a single housing to provide smoke activity accurately monitored by photoelectric sensing technology and thermal activity accurately monitored by thermistor sensing technology. UL & FM Listed | Comply
|  | b. Individual sensor information shall be processed by the host fire alarm control unit to determine sensor status and to determine whether conditions are normal, off-normal, or alarm. | Comply
|  | c. Combination smoke and heat sensors Rate-of-rise temperature characteristic shall be selectable at fire-alarm control unit for 15 or 20 deg F (8 or 11 deg C) per minute. | Comply
|  | d. The fixed-temperature sensing shall be independent of rate-of-rise sensing and shall be settable at fire-alarm control unit to operate at 135 or 155 deg F (57 or 68 deg C). | Comply
|  | e. Bases: CO Sensor, relay output, sounder, and isolator bases shall be supported alternatives to the standard base. | Comply
818.3.19 ADDRESSABLE INTERFACE MODULES
|  | a. Arrange to monitor or control one or more system components that are not otherwise equipped for addressable communication | Comply
|  | b. Modules shall be used for monitoring of waterflow, valve tamper, non-addressable devices, and for control of AHU systems. | Comply
|  | c. All Circuit Interface Modules shall be supervised and uniquely identified by the control unit. | Comply
|  | d. Module identification shall be transmitted to the control unit for processing according to the program instructions. | Comply
|  | e. Modules shall have an on-board LED to provide an indication that the module is powered and communicating with the FACU. | Comply
818.3.20 Fault Isolator Modules - UL & FM Listed
|  | a. Fault isolator modules shall detect and isolate a short-circuited segment of a fault-tolerant loop. | Comply
|  | b. The module shall automatically detect a return-to-normal condition of the loop and restore the isolated segment | Comply
|  | c. Modules shall be provided for every 20 field addressable devices to limit the extent of devices affected in the event of a short-circuit. | Comply
d. A minimum of two fault isolator modules shall be provided for one detection line loop
818.3.21 Notification Devices (Conventional) - UL & FM Listed
|  | a. Horn: Piezoelectric type horn shall be listed to UL 464. The horn shall have a minimum sound pressure level of 85 dBA @ 24VDC. | Comply
|  | b. Visible/Only Strobe: Strobe shall be listed to UL 1971. The V/O shall consist of a xenon flash tube and associated lens/reflector system. V/O appliances shall be provided with different minimum flash intensities of 15cd, 30cd, 75cd and 110cd. | Comply
|  | c. High Intensity Visible/Only Strobe: Strobe shall be listed to UL 1971. The V/O shall consist of a xenon flash tube and associated lens/reflector system. V/O appliances shall be provided with different minimum flash intensities of 135cd, 177cd and 185cd. | Comply
|  | d. Combination Audible/Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe light shall consist of a xenon flash tube and associated lens/reflector system. The horn shall have a minimum sound pressure level of 85 dBA @ 24VDC. | Comply
|  | e. High Intensity Combination Audible/Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe light shall consist of a xenon flash tube and associated lens/reflector system. Strobe appliances shall be provided with different minimum flash intensities of 135cd, 177cd and 185cd. The horn shall have a minimum sound pressure level of 85 dBA @ 24VDC. | Comply
|  | f. Multi-Tone Audible Only: Multi-tone appliance shall be listed to UL 464. Per appliance tone selection of 520 Hz Horn, Broadband Horn, Bell, Chime, High/Low, Slow Whoop, or Siren shall be selected using an on-board DIP Switch. Output level shall be selectable as high or low. 520 Hz tone shall be compliant with NFPA 72 Low Frequency Signal Requirements for Sleeping Areas. | Comply
|  | g. Multi-Tone Audible/Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe light shall consist of a xenon flash tube and associated lens/reflector system and shall be provided with different minimum flash intensities of 15cd, 30cd, 75cd, 110cd, 135, and 185 candela. Multi-tone appliance shall be listed to UL 464. Per appliance tone selection of 520 Hz Horn, Broadband Horn, Bell, Chime, High/Low, Slow Whoop, or Siren shall be selected using an on-board DIP Switch. Output level shall be selectable as high or low. 520 Hz tone shall be compliant with NFPA 72 Low Frequency Signal Requirements for Sleeping Areas. | Comply
|  | h. Weatherproof Visible Only shall be UL 1971 listed for indoor applications with strobe intensity selectable as 15, 60, or 75 cd or UL 1638 listed for outdoor applications with strobe rated at 75 cd (WP75). The appliances shall be acceptable for indoor and outdoor, extended temperature and extended humidity applications. The V/O device shall consist of a xenon flash tube and associated lens/reflector system, weatherproof cover and weatherproof mounting box. The Candela levels shall be selectable by using a hardware selector on the appliance. | Comply
|  | i. Weatherproof Audible/Visible shall be UL 464 and UL 1971 listed for indoor applications with strobe intensity selectable as 15, 60, or 75 cd or UL 1638 listed for outdoor applications with strobe rated at 75 cd (WP75). The appliances shall be acceptable for indoor and outdoor, extended temperature and extended humidity applications. The A/V device shall consist of a xenon flash tube and associated lens/reflector system, weatherproof cover and weatherproof mounting box. The Candela levels shall be selectable by using a hardware selector on the appliance. The Horn shall support Temporal Code 3, March Time (20, 60, or 120 BPM), Continuous, and Temporal Code 4 coding patterns. The horn shall have a minimum sound pressure level of 79 dBA for coded operation at 24 VDC. | Comply
|  | j. Notification Appliance Circuit provides synchronization of strobes at a rate of 1Hz and operates horns with the selected tone operation. The circuit shall provide the capability to silence the audible signals, while the strobes continue to flash, over a single pair of wires. The capability to synchronize multiple notification appliance circuits shall be provided. | Comply
818.3.22 Pre Commissioning Test Report
|  | The supplier shall submit a report prior to full acceptance to ensure all loops are tested for ground, short, open circuits and all address are set correctly. The supplier can bring a small panel or equipment to test full or partial loop to generate a report to pre arrest and fix all potential issues before Ceiling is up. A proper report to be submitted at quarterly interval of installation from 20%, 40%, 60% and 80% of installed devices and wired run. | Comply
818.3.23 Battery Charger and Batteries
|  | a. A 24 V DC trickle type battery charger and batteries shall be provided next to the fire alarm panel. The battery shall be of the maintenance free sealed lead acid (SLA) type. | Comply
|  | b. Battery charging equipment shall incorporate automatic control features with output designed to charge and maintain the cells within the limits specified by the battery manufacturer taking into account any quiescent load imposed by the associated system. Loss of effective battery capacity shall be recognized during the course of routine test of the batteries | Comply
|  | c. Each battery of secondary cells used in the equipment when charged for a period of 24 hour from fully discharged condition, shall then have sufficient available power to supply the quiescent load together with any fault signals resulting from power supply for a period of 72 hours. Thereafter, it shall be capable of supplying an additional load resulting from an alarm originating in two separate zones for a period of 1 hour, and it shall in addition be capable of supplying the full emergency evacuation alarm load for a period of at least 1 hour. | Comply
|  | d. In selection of battery capacity, a deterioration factor of 0.9 minimum shall be applied. | Comply
|  | e. The manufacturer of the control equipment shall provide information on the basis of the derivation of those combinations of battery charging equipment and batteries that meet the above requirements for any system into which the control equipment is to be incorporated. | Comply
|  | f. The initial charging of the battery cells shall be carried out in accordance with the manufacturer's instructions. | Comply
818.3.24 Testing and Commissioning
|  | a. A general check of all the equipment shall be made and shall include a check of dimensions, location and routing, and the completeness, correctness and condition of earth connections, labeling, clearances, painted surfaces, cables, wiring, pipe work, blanking plates and all other auxiliary and ancillary items. | NOTED
|  | b. All fire alarm systems shall be tested , prior to final acceptance testing, in accordance with the requirements of the design standards and specifications. | NOTED
|  | c. System testing shall include operational and supervisory testing of all control equipment, indication devices, detectors, indicating appliances, fireman's telephones, remote signalling apparatus, auxiliary functions, system wiring, with the final iteration of the system software installed in non-volatile memory. | NOTED
|  | d. All system testing shall be conducted in accordance with the approved test protocols. Written test protocols including detailed test procedures, documentation sheets and expected test results shall be submitted to the Employer’s Representative for approval. | NOTED
| 818.3.25 | Acceptance Testing
|  | - A final acceptance test of the fire alarm system components shall be performed in the presence of the Employer’s Representative and the Jabatan Perkhidmatan Bomba Malaysia (JBPM). This test shall be scheduled by the Employer’s Representative and Employer upon completion of the work (excluding tenant work), after receipt, review and acceptance of the system Certification of contractor testing. | Comply

## FireDet & Addr Notification
1 | FIRE ALARM AND DETECTION SYSTEM
1.1 | General
| The fire alarm & detection system shall be an intelligent analogue expandable addressable type. The fire alarm & detection system shall be designed, installed and commissioned to achieve the following functions: i) Fire Alarm Systems with Network ii) Integrated Emergency voice communication(As Required) v) Mimic panel shall be provided for" a. Building General Fire Alarms b. Building Pressurization Fans Status (As required Item iv) c. Building Car Park Fans Status( As required item iv) d. Other Key equipment controlled by the Fire Alarm Systems iv) Integrated Multiplex Fan Control systems from the fire Alarm panel(As Required) iii) Integrated Fireman’s telephone system or equivalent(As Required) |  | Comply
| The fire alarm and detection system shall comprise of , main fire alarm panel, repeater fire alarm panel, initiating devices, manual call points, notification signaling devices, multiplex fan control interface, wiring and all related accessories based on the most recent proven technology for both hardware and software to implement complete and functional systems designed to meet the requirements as outlined in this specification. |  | Comply
| The fire alarm & detection system shall commissioned by the specialist supplier of the manufacturer as per chapter 10 of NFPA72. To ensure proper function of the complete system to the satisfaction and approval of the relevant Fire Authority and Employer. |  | Comply
| The main fire alarm panel and the detectors or interface shall be of proprietary type. All system hardware and software shall be of a type already widely used for this field of application with at least 10 years of previous installed records in Malaysia. |  | Comply
1.2 | Standards
Relevant Codes and Standards:
| Product Performance UL 864, Fire Detection and Control (UOJZ), Minimum UL268 6th edition for Detectors Smoke Control Service (UUKL), Releasing Device Service (SYZV) FM Approved Requirement of Jabatan Bomba Dan Penyelamat Malaysia |  | Comply
| Codes and Standards NFPA72 2016/2019 Fire Detection, Voice Evac Installation, Operation and Service Codes NFPA92,92A & 92B Smoke Control systems Other codes and regulations of the local jurisdictional authorities |  | Comply
1.3 | Technical and Installation Requirements
System Description and Operation
|  | The fire alarm system shall incorporate the latest microcomputer technology and shall be able to achieve a satisfactory long life span. The system shall be compatible with future product upgrading and expansion. It shall also be easily integrated to other computer based systems. The system shall have the following operational features: | Comply
|  | a. The system shall automatically set the number of addresses in the system with Dip switch or equivalent. Software address not acceptable | Comply
|  | b. The address should be on the base to simplified detector cleaning operation | Comply
|  | c. The system shall be able to provide more than one level of dirt warning besides Prealarm and able to list out to clean only detector that requires cleaning for example almost dirty, dirty, excessively dirty..etc | Comply
|  | d. The system shall be able to swop Smoke with Heat detector with only trouble condition indicated on panel and revert to normal when replaced with the right detector. The heat detector when swop will be recognised by the Fire alarm panel and function accordingly. The purpose is for minor renovation work with minimum engineering cost involved and maximum life safety protection. | Comply
|  | e. It shall incorporate an alarm organization feature should it be desired to raise an alarm only if any two smoke or heat detectors are activated. | Comply
|  | f. It shall also be able to automatically store and print out upon command all detectors highest sensitivity activated versus the setpoint in their allocated environment. | Comply
|  | g. Print-outs of all types of condition shall have the date and time or occurrence. | Comply
|  | h. The main panel shall be able to show or print out the sensitively level of any detectors in the system. | Comply
|  | i. First alarms shall always to be top priority and remain in the display screen until reset. | Comply
|  | j. To allow interfacing of non-addressable devices into the main system and flow-switches thru interface modules. | Comply
|  | k. The sensitivity of all detectors shall be able to be adjusted individually at the panel and the detector itself. | Comply
|  | l. The system shall be compact stand-alone unit and capable of expanding by networking with additional Sub Alarm panels in the field as required for up to 99 panels or Workstation Servers | Comply
|  | m. The network communication shall have both option of normal hardwired base standard speed communication(9.6kBd to 57.6Kbd) or option for IP base high speed Communication and able to support Single mode fibre optic communication speed of minimum 100mbs. | Comply
|  | n. The systems shall support Graphic Workstation Server with minimum of 20 supervised or unsupervised Clients Workstation. It shall have the option of support mobile clients for both Android and Iphone and a one time mobile Client charges on the Server. There is no limitation of nos of mobile clients connections. | Comply
|  | o. The systems shall have the option of adding modules for a integrated voice evacuation and fire man phone solution. | Comply
|  | p. To provide self-diagnostic features for various system faults. | Comply
|  | q. The system shall have a minimum capacity of up to 10 loops with each loop catering for minimum 250 addressable device of any mix of Detectors or modules. | Comply
1.4 |  | Quality Control
|  | a. Installer Qualifications: A factory certified and trained engineer is to supervised the installation contractor on the work of this section. | Comply
|  | b. Each and every item of the Fire Alarm System shall be listed under the appropriate category by UL and FM and shall bear the respective label. | Comply
MAINTENANCE SERVICE
|  | a. Warranty Maintenance Service: Provide maintenance of fire alarm systems and equipment for a period of 12 months, using factory-authorized service representatives | Comply
|  | b. Basic Services: Routine maintenance visits on an “as needed” basis at times scheduled with the Owner. | Comply
|  | c. Additional Services: Perform services within the above 12-month period not classified as routine maintenance or as warranty work when authorized in writing. Compensation for additional services must be agreed upon in writing prior to performing services. | Comply
|  | d. Maintenance Service Contract: No later than 60 days prior to the expiration of the warranty maintenance services, deliver to the Owner a proposal to provide contract maintenance and repair services for an additional one-year term. | Comply
1.5 |  | Fire Alarm Panel
|  | a. General: Comply with UL 864, "Control Units and Accessories for Fire Alarm Systems". UL & FM Listed The following FACU hardware shall be provided: | Comply
|  | b. Network pathways shall support RS485 hardwired, fiber optic (Single or multimode) and RJ45 as needed. | Comply
|  | c. All Fire Panel Provided need to Comply with NFPA72 Class X requirements and minimum communication speed of 12Mbps for hardwired connection. | Comply
|  | d. All Fire Alarm panels shall come with UL and FM Listing with supporting documents. | Comply
|  | e. The supplier must be able to Comply to NFPA72 2016 Chapter 7 for all documentations and NFPA72 2016 Chapter 10 for qualified manpower provision in the various stage from installations till handover. | Comply
|  | f. Able to support up to minimum of 99 Network nodes | Comply
|  | g. All Panels shall come with 32Bit CPU and with a build in minimum of 2 GB Memory card to store the related system documentation such as record drawings, record of completion, owner’s manuals, testing and maintenance records, and backup of database ….etc. or equivalent. Minimum enclosure rating shall be not less than NEMA 1 or IP30 rating. | Comply
|  | h. Minimum Panel addressable capacity shall not be less than 2,500 points that can support capacity of 2,000 addressable detectors and 500 addressable modules. Suppliers with higher point count are acceptable with minimum detector capacity as specified. | Comply
|  | i. Minimum Loop capacity shall not be less than 10 loops or greater. | Comply
|  | j. Addressable Device loops shall support non shielded or non-screen cables of recommended factory wire gauge | Comply
|  | k. The systems provided should have proven documentation by the manufacturer to prove history of backward and forward compatible records for both Panel and Devices to protect the interest of the end user. | Comply
|  | l. The system shall be provided with sufficient battery capacity to operate the entire system upon loss of normal AC power in a normal supervisory mode for a period of 24 hours with 5 minutes of alarm. | Comply
|  | m. Able to provide Integrated Voice Evacuation if function is required in future and for supplier without this feature shall provide 100 zones of input and output modules as default. | Comply
Fireman phone
|  | a. Firefighter's Phone: Provide a supervised, two-way communication system phones between the Command Center/main fire alarm control unit and emergency | Comply
|  | b. The firefighter's phone system shall be capable of handling single or simultaneous conversations with all phones connected into the system. | Comply
|  | c. As many as six phones shall be able to be connected into the active conversation. | Comply
|  | d. The act of plugging a handset into an emergency phone jack or removal of any phone from its normal hook position shall cause an audible and visual indication control unit. | Comply
System Printer
|  | a. Provide a 80 or 132 column dot-matrix type, listed and labeled as an integral part of the fire alarm system. | Comply
1.6 |  | Network Annunicator Repeater
|  | a. The Repeater or Annunicator shall be a Network type and not dependant only on Main Fire Alarm Panel. | Comply
|  | b. Network pathways shall support RS485 hardwired, fiber optic (Single or multimode) and RJ45 as needed. | Comply
|  | c. All Repeater Panel Provided need to Comply with NFPA72 Class X requirements and minimum communication speed of 12Mbps for hardwired connection. | Comply
|  | d. All Repeater panels shall come with UL and FM Listing with supporting documents. | Comply
GRAPHIC MIMIC ANNUNCIATOR - LED TYPE
|  | a. Annunciator Unit, zoned system: Provide an LED-indicating light located on the floor plan for each zone. For each zone, mark zone boundaries on the annunciator floor plan. | Comply
|  | b. Annunciator Unit, addressable system: Provide an LED-indicating light located on the floor plan for each device indicating the type of device and floor on which a signal was actuated floor plan for each device indicating the type of device and floor on which a signal was actuated. | Comply
|  | c. Provide individual LED indicators for each alarm and supervisory device or zone and a LED to indicate system trouble. Additional LEDs indicate normal power and emergency power modes for the system. A toggle or push-button switch tests the LEDs mounted on the unit. The test switch does not require key operation. and a LED to indicate system trouble. Additional LEDs indicate normal power and emergency power modes for the system. A toggle or push-button switch tests the LEDs mounted on the unit. The test switch does not require key operation. | Comply
|  | d. Enclosure: Finish to match Fire Alarm Control Units. The locking cover/display assembly is hinged on the left. Key and lock shall be common to all secured fire alarm system enclosures. | Comply
1.7 | NETWORK COMMAND GRAPHICAL WORKSTATION
|  | a. Able to support up to 100,000 Fire Detection points on a Workstation Server, it is not accepted to have multiple server as system operation integrity will be at risk. UL & FM Listed | Comply
|  | b. The 100,000 points shall be the full point count allocated to Fire Detection and not other systems. | Comply
|  | c. The workstation shall be linked to the Fire Alarm systems thru Class B RJ45 connections. | Comply
|  | d. PCI cards connections shall not be acceptable as they are old fashion and limited brands of support by computer supplier. | Comply
|  | e. Standard Video output for one LCD Display and able to add up to maximum of 4 LCD Display driven from one CPU Display driven from one CPU | Comply
|  | f. Each LCD Display is able to display a selected dedicated function with no interruptions from other functions e.g. Graphics only, Alarm and Fault only, History log only, IP Camera only….etc log only, IP Camera only….etc | Comply
|  | g. Integrated email Notification Service | Comply
|  | h. Field editor for graphics representations with ability to Import and Export AutoCAD graphic files | Comply
|  | i. Integrated web-page, web-camera, or web-link and able to manually display by IP address on windows or operated automatically upon Alarm points or zone | Comply
|  | j. It shall be possible to assign a different WAV file notification signal in the local language for each abnormal event. | Comply
|  | k. The Graphical Workstation shall have the capacity to annunciate 62,500 network point and/or point lists. | Comply
|  | l. Historical event logs shall maintain up to 500,000 system events. | Comply
|  | m. Built-in diagnostics shall provide graphical Diagnostic views of the network topology and status. | Comply
|  | n. Have option of both PCI Slot or can be mounted externally for network card. | Comply
|  | o. Capacity to create and edit up to 25,000 Graphic Screens. | Comply
|  | p. The Graphical Workstation shall come with both UL and FM Listing. | Comply
|  | q. Graphic Workstation shall not be a slave connected to Fire alarm panel to operate. | Comply
Comply
Remote Ethernet Client Support:
|  | a. The Graphical Workstation server shall be capable of supporting up to 20 Simultaneous Remote Client Connections over Ethernet. | Comply
|  | b. It shall be possible to vector information to Remote Supervised Clients by selecting.which points and/or event categories (Alarm, Priority 2, Supervisory, Trouble) are to be displayed at each Remote Supervised Client. | Comply
1.8 | Mobile client Support
|  | a. The Graphical Workstation shall support both Apple iPhones and iPads, and Android phones and tablets. | Comply
|  | b. This support shall include providing fire alarm network annunciation and limited control through a compatible 3G and 4G cellular service via VPN (virtual private network) connection. | Comply
|  | c. Mobile Client Support shall connect an essentially unlimited number of Mobile Clients for simultaneous status information access. | Comply
|  | d. Limited control function shall be accessible by password controlled login and by designated mobile device. | Comply
|  | e. Display of Fire Alarm /Priority 2/Supervisory/Trouble conditions via active lists in separate tabs selection. | Comply
|  | f. Access to system silence and reset panel and Voice evac with additional level of user name and password. | Comply
Spare capacity
|  | Sufficient installed spare capacity shall be provided to enable the system functionality to be increased as follows: | Comply
|  | a. 20% spare detection Device loop capacity per Panel. This requirement shall ensure that all the fire alarm panels have the spare capacity to accommodate additional loops without the requirement for upgrading the complete control panel. | Comply
|  | b. 20% spare detection device capacity per loop for both Detectors and Modules Device. This requirement shall ensure that additional detection devices can be fitted to existing loops (within the restrictions of manufacturers maximum permitted loop lengths). | Comply
|  | c. 20% spare Notification circuits for any future expansion requirements by the Fire Alarm Panels. | Comply
ADDRESSABLE INITIATING - PullStation
|  | a. General Requirements for Manual Fire-Alarm Boxes: Comply with UL 38. Boxes shall be finished in red. UL & FM Listed | Comply
ADDRESSABLE INITIATING - Detectors
ADDRESSABLE ANALOG SMOKE SENSORS
|  | a. Comply with Minimum of UL 268 6th Edition and Self-Restoring. UL & FM Listed | Comply
|  | b. Removal of the detector head shall cause a trouble signal at the control unit. | Comply
|  | c. Sensor address shall be located in base to simplified operations when replacing sensors. | Comply
|  | d. Upon replacement of sensor head after cleaning shall operate immediately without intervention | Comply
|  | e. Environmental compensation, programmable sensitivity settings, status testing, and monitoring of sensor dirt accumulation shall be provided by the Fire control panel. | Comply
|  | f. Options of Full Black color detector for the head and base shall be at no increase of price and not minimum order quantities | Comply
1.9 | ADDRESSABLE INITIATING - In-DUCT SMOKE SENSOR
Addressable In-Duct Mounted Smoke Sensors - UL & FM Listed
|  | a. Photoelectric type, for applications with controlled dust and humidity providing HVAC duct smoke sensing where sampling tube designs are not appropriate. | Comply
|  | b.In-Duct housing shall include relay or relay driver as required for fan shutdown. | Comply
|  | c. Shall accommodate duct airflow from 0 to 4000 ft/min (0 to 1220 m/min), and provide environmental compensation, programmable sensitivity settings, status testing, and monitoring of sensor dirt | Comply
|  | d. Duct Housing shall have a transparent cover to monitor for the presence of smoke. | Comply
|  | e. Each duct smoke sensor shall be provided with a Remote Test Station with an alarm LED and test switch. | Comply
ADDRESSABLE INITIATING - Heat Detector
ADDRESSABLE HEAT SENSORS
|  | a. Comply with UL 521.- UL and FM Listed | Comply
|  | b.Thermal Sensor: Combination fixed-temperature and rate-of-rise unit with plug-in base and alarm indication lamp | Comply
|  | c. Full color Black color detector available for head and base. | Comply
|  | d. Rate-of-rise temperature detection is selectable 15° F (8.3° C) or 20° F (11.1° C) per minute. | Comply
|  | e. Fixed temperature sensing is independent of rate-of-rise sensing and programmable to operate at 135° F (57.2° C) or 155° F (68° C). | Comply
ADDRESSABLE CO SENSOR SOUNDER BASE - UL & FM Listed
|  | a. The CO Sensor Sounder base shall be listed to UL464, Audible Signal Appliances. | Comply
|  | b.CO sensor shall provide enhanced fire detection with the addition of two selectable modes of operation: Nuisance Alarm Reduction Mode and Faster Fire Detection. | Comply
|  | c. The CO Sensor Sounder Base shall include CO sensor element mounted in the sounder base which can be easily replaced without replacing the complete sensor base assembly. | Comply
|  | d. The CO Sensor Sounder base shall report the following CO Sensor troubles: Communication loss, Disabled, Almost Expired 12 Months, Almost Expired 6 Months, Expired (End of Life), and Sensor Missing/Failed. | Comply
|  | e. CO Base can be used with any combination of Heat only, Photo only or Photo and Heat. | Comply
ADDRESSABLE MULTI-POINT/MULTI-SENSOR/MULTI-CRITERIA SENSOR
|  | a. Smoke and heat sensing shall be available to be combined in a single housing to provide smoke activity accurately monitored by photoelectric sensing technology and thermal activity accurately monitored by thermistor sensing technology. UL & FM Listed | Comply
|  | b. Individual sensor information shall be processed by the host fire alarm control unit to determine sensor status and to determine whether conditions are normal, off-normal, or alarm. | Comply
|  | c. Combination smoke and heat sensors Rate-of-rise temperature characteristic shall be selectable at fire-alarm control unit for 15 or 20 deg F (8 or 11 deg C) per minute. | Comply
|  | d. The fixed-temperature sensing shall be independent of rate-of-rise sensing and shall be settable at fire-alarm control unit to operate at 135 or 155 deg F (57 or 68 deg C). | Comply
|  | e. Bases: CO Sensor, relay output, sounder, and isolator bases shall be supported alternatives to the standard base. | Comply
2.0 | ADDRESSABLE INTERFACE MODULES
|  | a. Arrange to monitor or control one or more system components that are not otherwise equipped for addressable communication | Comply
|  | b. Modules shall be used for monitoring of waterflow, valve tamper, non-addressable devices, and for control of AHU systems. | Comply
|  | c. All Circuit Interface Modules shall be supervised and uniquely identified by the control unit. | Comply
|  | d. Module identification shall be transmitted to the control unit for processing according to the program instructions. | Comply
|  | e. Modules shall have an on-board LED to provide an indication that the module is powered and communicating with the FACU. | Comply
Fault Isolator Modules - UL & FM Listed
|  | a. Fault isolator modules shall detect and isolate a short-circuited segment of a fault-tolerant loop. | Comply
|  | b. The module shall automatically detect a return-to-normal condition of the loop and restore the isolated segment | Comply
|  | c. Modules shall be provided for every 20 field addressable devices to limit the extent of devices affected in the event of a short-circuit. | Comply
d. A minimum of two fault isolator modules shall be provided for one detection line loop
2.1 | ADDRESSABLE NOTIFICATION - UL & FM Listed
1. ADDRESSABLE ALARM NOTIFICATION APPLIANCES Addressable Notification Appliances: The Contractor shall furnish and install Addressable Notification Appliances and accessories to operate on compatible signaling line circuits (SLC).
|  | a. All Notification Appliances shall operate as a completely independent device allowing for appliances in handicap accessible rooms and other locations to operate on the same SLC and to activate individually based on an alarm condition in a room or as part of a general alarm condition where all appliances activate together. | Comply
|  | b. Individual Notification Appliances shall be able to be grouped into zones (or operational groups) by central programming at the main fire alarm control unit. | Comply
|  | c. Notification Appliances shall provide for “unobtrusive” testing. | Comply
|  | d. Each Notification Appliance shall be tested for audible and visible operation on an individual basis at the device or from the main fire alarm control unit, allowing for minimal invasive impact. | Comply
2. Pre Test Report for Individual Loop Prior to acceptance Test for Notification Circuits and Devices.
|  | a. The supplier shall submit a report prior to full acceptance to ensure all loops are tested for ground, short, open circuits and all address are set correctly. | Comply
|  | b. The supplier can bring a small panel or equipment to test full or partial loop to generate a report to pre arrest and fix all potential issues before Ceiling is up. | Comply
|  | c. A proper report to be submitted at quarterly interval of installation from 20%, 40%, 60% and 80% of installed devices and wired run. | Comply
2.2 | 3. DIFFERENT TYPES OF ADDRESSABLE NOTIFICATION DEVICES
|  | a. Addressable Horn: Addressable horn shall be listed to UL 464. Horn shall support Temporal Code 3, March Time (20, 60, or 120 BPM), Continuous, and Temporal Code 4 coding patterns. Horn appliances shall have a High/Low Setting, programmable by channel from the addressable controller or by appliance from the host FACU. The horn shall have a minimum sound pressure level of 83 or 89 dBA for steady) or of 79 or 85 dBA for coded operation. | Comply
|  | b. Xenon Flasher Addressable Visible/Only: Addressable strobe shall be listed to UL 1971. The V/O device shall consist of a xenon flash tube and associated lens/reflector system, cover and mounting plate. The V/O appliance shall be provided with multiple minimum flash intensities of 15cd, 30cd, 75cd, 110cd, 135cd and 185cd. The Candela levels shall be settable from the fire alarm control unit or by using a hardware selector on the appliance. | Comply
|  | c. Xenon Flasher Addressable Audible/Visible Addressable combination Audible/Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe device shall consist of a xenon flash tube and associated lens/reflector system, cover and mounting plate. The strobe shall provide multiple minimum flash intensities of 15cd, 30cd, 75cd, 110cd, 135cd and 185cd. The Candela levels shall be settable from the fire alarm control unit or using a hardware selector on the appliance. The Horn shall support Temporal Code 3, March Time (20, 60, or 120 BPM), Continuous, and Temporal Code 4 coding patterns. The horn shall have a minimum sound pressure level of 83 or 89 dBA for steady or 79 or 85 dBA for coded operation. The appliance shall be capable of two-wire synchronization with one of the following options: o Synchronized Strobe with Horn on steady. o Synchronized Strobe with Temporal Code Pattern on Horn. o Synchronized Strobe with March Time cadence on Horn. o Synchronized Strobe firing to NAC sync signal with Horn silenced. | Comply
|  | d. Addressable Multi-Tone Audible Only: Addressable multi-tone appliance shall be listed to UL 464. Per appliance tone selection of 520 Hz Horn, Broadband Horn, Bell, and Chime tones shall be controlled as Temporal Code 3, Temporal Code 4, March Time (selectable as 20, 60, or 120 bpm), or Continuous shall be programmable from the control panel, or selected using an on-board DIP Switch. Slow Whoop, Siren, and High/Low tone selections shall be controlled as synchronized continuous operation. Appliances shall have a High/Low Setting, programmable by channel from the addressable controller or by appliance from the host FACU. | Comply
|  | e. Xenon Flasher Addressable Multi-Tone Audible/Visible: Addressable combination Multi-Tone Audible/Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe device shall consist of a xenon flash tube and associated lens/reflector system, cover and mounting plate. The strobe shall provide multiple minimum flash intensities of 15cd, 30cd, 75cd, 110cd, 135cd and 185cd. The Candela levels shall be settable from the fire alarm control unit or using a hardware selector on the appliance. Per appliance tone selection of 520 Hz Horn, Broadband Horn, Bell, and Chime tones shall be controlled as Temporal Code 3, Temporal Code 4, March Time (selectable as 20, 60, or 120 bpm), or Continuous shall be programmable from the control panel, or selected using an on-board DIP Switch. Slow Whoop, Siren, and High/Low tone selections shall be controlled as synchronized continuous operation. Appliances shall have a High/Low Setting, programmable by channel from the addressable controller or by appliance from the host FACU. | Comply
2.3 |  | f. Xenon Flasher Addressable Weatherproof Visible Only: (Outdoor Applications) Addressable weatherproof strobe shall be UL 1971 listed for indoor applications with strobe intensity selectable as 15 or 75 cd or UL 1638 listed for outdoor applications with strobe rated at 75 cd (WP75) or 185 cd (WP185). The appliances shall be acceptable for indoor and outdoor, extended temperature and extended humidity applications. The V/O device shall consist of a xenon flash tube and associated lens/reflector system, weatherproof cover and weatherproof mounting box. The V/O appliance shall be provided with multiple minimum flash intensities of 15, 75, WP 75, or WP 185 candela. The Candela levels shall be settable from the fire alarm control unit or by using a hardware selector on the appliance. | Comply
|  | g. Addressable Weatherproof Audible/Visible: Addressable weatherproof horn/strobe shall be UL 464 and UL 1971 listed for indoor applications with strobe intensity selectable as 15 or 75 cd or UL 1638 listed for outdoor applications with strobe rated at 75 cd (WP75) or 185 cd (WP185). The appliances shall be acceptable for indoor and outdoor, extended temperature and extended humidity applications. The strobe appliance shall be provided with multiple minimum flash intensities of 15, 75, WP 75, or WP 185 candela. The Candela levels shall be settable from the fire alarm control unit or by using a hardware selector on the appliance. The Horn shall support Temporal Code 3, March Time (20, 60, or 120 BPM), Continuous, and Temporal Code 4 coding patterns. The horn shall have a minimum sound pressure level of 81 or 87 dBA for steady or 80 or 87 dBA for coded operation. | Comply
|  | h. LED Addressable Visible Only for >110 Cd Requirements lower current drawn. Addressable LED visible strobe (V/O) shall be listed to UL 1971. The multi-candela LED V/O strobe device shall be available in low (15, 30, 75 cd) and high (110, 135, 185 cd) range candela. Models shall provide a small compact design with low current draw due to efficient strobe LED’s. LED strobe device shall consist of two pieces; cover and appliance/mounting plate. Synchronized LED strobe operation shall be provided with other LED or Xenon strobe devices on the same circuit or the same panel on different circuits. LED strobe device shall meet the 20ms pulse width requirement in the 2016 Edition of NFPA 72. The Candela levels shall be settable from the fire alarm control unit or by using a hardware selector on the appliance. Weatherproof model shall mount to provided single gang weatherproof electrical box. | Comply
|  | i. LED Addressable Audible/Visible for > 110 Cd Requirements lower current drawn Addressable combination LED Audible/Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. Horn shall support Temporal Code 3, March Time (20, 60, or 120 BPM), Continuous, and Temporal Code 4 coding patterns. Horn shall have a High/Low Setting, selectable at the appliance or programmable from the addressable controller by appliance from the host FACU. The horn shall have a minimum sound pressure level of 85 or 87 dBA for steady) or of 81 or 83 dBA for coded operation. The multi-candela LED V/O strobe device shall be available in low (15, 30, 75 cd) and high (110, 135, 185 cd) range candela. Models shall provide a small compact design with low current draw due to efficient strobe LED’s. Synchronized LED strobe operation shall be provided with other LED or Xenon strobe devices on the same circuit or the same panel on different circuits. LED strobe device shall meet the 20ms pulse width requirement in the 2016 Edition of NFPA 72. | Comply
2.4 |  | j. Addressable Notification Circuits Isolator Module: For every 20 Addressable Circuits Fault Isolation Isolator module provides short circuit isolation for addressable notification appliance SLC wiring. Isolator shall be listed to UL 864. The following functionality shall be included in the Isolator module: Report faults to the host FACU. o On-board Yellow LED provides module status. o After the wiring fault is repaired, the Isolator modules shall test the lines and automatically restore the connection. | Comply
Pre Commissioning Test Report
|  | The supplier shall submit a report prior to full acceptance to ensure all loops are tested for ground, short, open circuits and all address are set correctly. The supplier can bring a small panel or equipment to test full or partial loop to generate a report to pre arrest and fix all potential issues before Ceiling is up. A proper report to be submitted at quarterly interval of installation from 20%, 40%, 60% and 80% of installed devices and wired run. | Comply
Battery Charger and Batteries
|  | a. A 24 V DC trickle type battery charger and batteries shall be provided next to the fire alarm panel. The battery shall be of the maintenance free sealed lead acid (SLA) type. | Comply
|  | b. Battery charging equipment shall incorporate automatic control features with output designed to charge and maintain the cells within the limits specified by the battery manufacturer taking into account any quiescent load imposed by the associated system. Loss of effective battery capacity shall be recognized during the course of routine test of the batteries | Comply
|  | c. Each battery of secondary cells used in the equipment when charged for a period of 24 hour from fully discharged condition, shall then have sufficient available power to supply the quiescent load together with any fault signals resulting from power supply for a period of 72 hours. Thereafter, it shall be capable of supplying an additional load resulting from an alarm originating in two separate zones for a period of 1 hour, and it shall in addition be capable of supplying the full emergency evacuation alarm load for a period of at least 1 hour. | Comply
|  | d. In selection of battery capacity, a deterioration factor of 0.9 minimum shall be applied. | Comply
|  | e. The manufacturer of the control equipment shall provide information on the basis of the derivation of those combinations of battery charging equipment and batteries that meet the above requirements for any system into which the control equipment is to be incorporated. | Comply
|  | f. The initial charging of the battery cells shall be carried out in accordance with the manufacturer's instructions. | Comply
Testing and Commissioning
|  | a. A general check of all the equipment shall be made and shall include a check of dimensions, location and routing, and the completeness, correctness and condition of earth connections, labeling, clearances, painted surfaces, cables, wiring, pipe work, blanking plates and all other auxiliary and ancillary items. | NOTED
|  | b. All fire alarm systems shall be tested , prior to final acceptance testing, in accordance with the requirements of the design standards and specifications. | NOTED
|  | c. System testing shall include operational and supervisory testing of all control equipment, indication devices, detectors, indicating appliances, fireman's telephones, remote signalling apparatus, auxiliary functions, system wiring, with the final iteration of the system software installed in non-volatile memory. | NOTED
|  | d. All system testing shall be conducted in accordance with the approved test protocols. Written test protocols including detailed test procedures, documentation sheets and expected test results shall be submitted to the Employer’s Representative for approval. | NOTED
Acceptance Testing
|  | - A final acceptance test of the fire alarm system components shall be performed in the presence of the Employer’s Representative and the Jabatan Perkhidmatan Bomba Malaysia (JBPM). This test shall be scheduled by the Employer’s Representative and Employer upon completion of the work (excluding tenant work), after receipt, review and acceptance of the system Certification of contractor testing. | Comply

## Technical Data Compliance
TECHNICAL DATA
Project Name: |  | Date Submitted
S/No | Fire Detection Solutions | Offered | Remarks
A | Fire Alarm Panel
1 | Make
2 | Country of Origin
3 | Model
4 | Dimensions (mm)
5 | LCD
6 | No. of Loop
7 | Initiating Address per loop
8 | Modules Address per loop
9 | Total Panel Point Capacity
10 | Finish / Material
11 | Gauge
12 | Ambient Temp
13 | Humidity
14 | Authority Listed
15 | Max. Wiring Distance
16 | Battery Charger
17 | Type (Battery Charger) | :
18 | Power Supply
19 | Local Agent
20 | Bomba Certificate
B | Breakglass
1 | Make
2 | Model
3 | Dimensions (mm)
4 | Current Consumption
5 | Alarm
6 | Operating Temperature
7 | Humidity
8 | Finish / Material
C | Addressable Smoke Detector
1 | Make
2 | Model
3 | Method of Addressing
4 | Operating Humidity
5 | Operating Temp
6 | Sensitivity
7 | Authority Listed
8 | Current Consumption
9 | Alarm
10 | Material
11 | Weight
D | Addressable Heat Detector
1 | Make
2 | Model
3 | Method of Addressing | :
4 | Operating Humidity
5 | Operating Temp
6 | Sensitivity
7 | Authority Listed
8 | Current Consumption
9 | Alarm
10 | Material
11 | Weight
E | Addressable Control Module
1 | Make
2 | Model
3 | Dimensions (mm)
4 | Material
5 | Operating Temp
6 | Humidity Range
7 | Authority Listed
8 | Current Consumption
F | Addressable Monitor Module
1 | Make
2 | Model
3 | Dimensions (mm)
4 | Material
5 | Operating Temp
6 | Humidity Range
7 | Authority Listed
8 | Current Consumption
G | Addressable Zone Module
1 | Make
2 | Model
3 | Dimensions (mm)
4 | Material
5 | Operating Temp
6 | Humidity Range
7 | Authority Listed
8 | Current Consumption
H | Notification Device
1 | Make
2 | Model
3 | Dimensions (mm)
4 | Material
5 | Operating Temp
6 | Humidity Range
7 | Authority Listed
8 | Current Consumption
I | Printer
1 | Make
2 | Country of Origin
3 | Model
4 | Dimensions (mm)
5 | Weight
6 | Column
7 | Printing Speed
J | Mimic
1 | Make
2 | Type
3 | Dimensions (mm)
K | Graphic Workstation Server
1 | Computer
2 | Make
3 | Model
4 | Country of Origin
5 | Processor Type
6 | Memory Capacity
7 | Speed
8 | HDD Capacity
9 | Interface Standard
L | SVGA Colour Monitor
1 | Make
2 | Country of Origin
3 | Type/Model
4 | Size
5 | Screen Resolution
6 | No. of colours
M | KEYBOARD
1 | Make
2 | Country of Origin
3 | Type/Model
4 | Keyboard layout
5 | Control function keys
M | Graphic Workstation Software
1 | Make
2 | Country of Origin
3 | Type/Model
4 | Authorities Listed
5 | Point Count Supported in offer
6 | Nos of Clients Supported
7 | Mobile Client Supported
8 | Autocad import Supported
9 | Maximum nos of Monitors Supported @ CPU